## Slide 1: Status of work on the cryostat design
Evgeny Koshurnikov
CERN
September 19, 2014
Joint Institute for Nuclear Research (Dubna)

## Slide 2: Cryogenic scheme
17 l/hour (0.6 g/sec) - cooling of the current leads
SF of 1.5

## Slide 3: Cooling Mode

## Slide 4: Forced flow cooling

## Slide 5: Natural convection

## Slide 6: Natural circulation cooling
H1
(D1, F1)
H2
(D2, F2)
H3
(D3, F3)
Driving force
density of the liquid helium in the supply tube
mean density of the liquid-vapor mixture in the heated tube
mean density of the liquid-vapor mixture in the return tube
2. The driving force balances against the pressure drops (friction and fluid acceleration)
- the acceleration pressure drop
G – flow of the helium, kg/sec
- density of the saturated vapor helium, kg/m3
- density of the saturated liquid helium, kg/m3
- vapor quality at the outlet of the heated tube
- vapor quality at the inlet of the heated tube
Schematic of a conventional natural circulation loop

## Slide 7: Friction pressure drop
- the friction pressure drop in the supply tube
– friction factor in the supply tube for liquid helium
f1=f (Re, G)
- the friction pressure drop in the heated tube
- the two-phase friction multiplier
viscosity of the saturated liquid helium, Pa*s,
viscosity of the saturated vapor helium, Pa*s
- the friction pressure drop in the return tube

## Slide 8: Computation of the mass flow rate
16.6 (36.6) W
(Pa)
, g/sec
Flow for one rib of the
heat exchanger with local singularities of the loop
Total flux for all ribs = 68 g/sec

## Slide 9: Assembled solenoid and control Dewar

## Slide 10: Cooling system

## Slide 13: Tubes of upper and bottom collectors. Radial suspension ties (top view)
~4.5 mm
Can we allow the unfixed cryogenic side of the cold mass with current leads and tubing to move a few millimeters while cooling?

## Slide 14: Tubes of upper and bottom collectors. Radia and axial suspension ties

## Slide 15: Control Dewar

## Slide 16: THANK YOU FOR YOUR ATTENTION!

## Slide 17: PANDA Target Spectrometer

## Slide 18: PANDA magnet in the experimental building (in-beam and in-parking positions)
Cold box of the liquefier and Buffer Dewar
Helium compressor
Radiation shield
LHe transfer line

## Slide 19: Space allocated for the Control Dewar
2345
Radiation shield

## Slide 20: Parameters of the axial suspension
*
Material of ties | Inconel 718 | 
Number of ties | 2 x 4 =8 | 
, MPa | 477 | 
Ø, mm | 20 | 
 | Estimate | 3D FE computations
σtemp ,MPa | 373 (78.2%) | 326.8
σprestr, MPa | 8.2 (1.7%) | 
σmag.force, MPa | 63.6 (13.3%) | 
% | 93.2% | 
Q4.2 , W | 1.05 | 
Q77 , W | 6.2 | 
Axial shift of the center, mm | 0.39 | 0.46
Material of ties | Inconel 718 | 
Number of ties | 2 x 4 =8 | 
 | 477 | 
Ø, mm | 20 | 
 | Estimate | 3D FE computations
σtemp ,MPa | 373 (78.2%) | 326.8
σprestr, MPa | 8.2 (1.7%) | 
σmag.force, MPa | 63.6 (13.3%) | 
 | 93.2% | 
Q4.2 , W | 1.05 | 
Q77 , W | 6.2 | 
Axial shift of the center, mm | 0.39 | 0.46

## Slide 21: Parameters of the radial suspension
Material of the ties | Inconel 718
Number of ties | 2 x 8 =16
, MPa | 477
Using Belleville springs | Yes
Ø, mm | 10
σtemp ,MPa | 335 (70%)
σprestr, MPa | -
σ weight+mag.force, MPa | 138.5 (29%)
% | 99%
Q4.2 , W | 1.1
Q77 , W | 6.6
Axial shift of the center under action of the magnetic decentering force, mm | 0.24
Material of the ties | Inconel 718
Number of ties | 2 x 8 =16
 | 477
Using Belleville springs | Yes
Ø, mm | 10
σtemp ,MPa | 335 (70%)
σprestr, MPa | -
σ weight+mag.force, MPa | 138.5 (29%)
 | 99%
Q4.2 , W | 1.1
Q77 , W | 6.6
Axial shift of the center under action of the magnetic decentering force, mm | 0.24