## Slide 1
Vacuum Control System and Interfaces to Accelerator Control System
Workshop on
“Controls Developments for FAIR Commissioning and the Operation of the existing Accelerator Complex”
A. Krämer for VAC
17.09.2020

## Slide 2: Introduction
Vacuum Control System is a close collaboration between ACO-IND and VAC.
Requirements are directly discussed with ACO-IND.
FAIR type Vacuum Controls System is already running at CRYRING and at UNILAC. Details were shown yesterday by Christine Betz.
Vacuum Control System works as stand alone system independent from Overall Accelerator Control System. Vacuum Control System has no requirements on timing or operation modes.
Operators can open/close valves and see the pressure value for each section, as well from the Vacuum Control System as also from the Accelerator Control System (tbd)
Full access only by experts.

## Slide 3: External Requirements / Open Points
Information delivered to overall control system: Interlocks, status of valves, vacuum pressures.
Access to additional data/values of pumps, gauges, valves to be discussed.
Additional signals/values required by overall accelerator control system to be defined by operations.
Signals required by other technical department to be defined by departments (e.g. pressure values for RF interlocks,…). The vacuum control system is prepared to deliver per section 1 analogue pressure value via a isolation amplifier (0…10V)
Exchange of signals/information required between Cryogenics – VAC have to be defined together with ACO-IND, this information can be exchanged via PLC to PLC communication
Other requests/requirements?

## Slide 4: Commissioning of vacuum controls:
Stepwise approach:
local test of gauges, pumps, valves per sector
manual tests of gauges, pumps, valves per sector from electronics rooms via long cables and controllers
remote test of gauges, pumps, valves system per sector via vacuum controls , test of procedures (pump down, venting,...)
remote test of functionality of corresponding vacuum sectors, test of procedures (pump down, venting,...) and interlocks
remote test of functionality of vacuum sectors machine overlapping
hand-over to operations
Commissioning with beam can only take place, when vacuum control system is in operation. Otherwise no interlocks, e.g. risk to shoot with beam on a closed valve.
Commissioning with beam not required by Vacuum Control System.