## Slide 1: Commissioning of Power Converters
H. Welker/EPS
17.09.2020

## Slide 2
Acceptance of Power Converters FAT + SAT (Aa-Ba)
  Acceptance tests will be performed with the power converter configuration software PCA as stand alone system. Generally no ACO hardware required or control system has to be available
  PCA includes:
    Semi automatic test procedure
    Generation of set values
    Generation of test reports
    Generation of configuration files
Commissioning of Power Converters

## Slide 3
Commissioning of Power Converters after Acceptance
New FESA-classes for new power converter topologies/functionalities required
Testing of control interface (preferably by automatized procedure)
  On/off/reset
  Supply of set values (I/U)
  Read back of actual values/status
Testing of interfaces to MPS (ΔI monitoring) and PAS
Synchronous operation of large power converters for power tests (i.e. SIS 100 main systems together with SIS 18 main systems). Partially in SAT Ab, Ba required.
Uploading of parameter files to central storage place (via the control system)
Commissioning of Power Converters

## Slide 4
Power converter data management / data exchange via control system
Write/read files to/from ACUs
  Firmware, parameter files & configuration files
    On demand to a single ACU
    Via broadcast to a list of ACUs
  Set internal ACU clock (time) once per day
Central storage of those files or interface to storage (database)
  Compare files stored in ACU with files stored on database
  In case of mismatch, actions to be taken have to be discussed in detail
  Accessible for EPS
Post mortem analysis
Commissioning of Power Converters