Topics:
  Design changes on
    gas tank fundament - in Room E40.310
&
      Adaptions inside the MVD-Pit
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	15.06.2021	1
[Speaker Notes: Topics The first part covers the design changes on the gas fundament and inside the Cryo compressor room. The last slide will deal with the actual space situation inside the MVD-Pit.]

---
 2. Adapted Design of the cryogenic apparatus outside the hall (GL01)
 E40.310
 GL 01
4
2
1
3
Housing for cryotech
N
- All components moved to the north
- Extension of fundament by 4m towards south
- piping conduit running inside hall from north
- He-Shield cooling combined with 2 evaporators/heaters
  (Saves N2 consumption)
- Aux.evaporator (4) keeps N2 supply line to Valve terminal
  dry (no condensation)
 Cryotechnical plant in outside region to be enclosed
Adaptions on concrete fundament
1. Main evaporator
2. HE-Shield cooling with Cold Box
3. Small Compressor
4. Auxiliary evaporator
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	2
  4m
[Speaker Notes: 2. Design of the cryogenic apparatus outside the hall (GL01) What are the changes regarding the apparatus in the outside region ? Firstly all cryogenic apparel has been moved to the north. The fundament for he gastanks will be extended by 4 m to the south and all the piping now enters the hall directly from the fundament. The nitrogen production will rely on two evaporators instead of only one. These are numbers (1) and (4). The auxiliary evaporator keeps the nitrogen line free of condensate so no insulation is needed. The combination of the Helium Shield cooling along with two evaporators saves nitrogen. A cover for the apparel outside is needed for protection against the atmosphere.]

---
 3. Adapted Design of the cryogenic apparatus inside Room E40.310
4
5
6
3
N
Adaptions in Room E40.310
1. Oil Separator
2. CWU (Cool Down Warm up unit, Connected with He-Shield)
3. auxiliary evaporator (New entry)
4. Main compressor
5. cooling water manifolds (access and return feed) (New entry)
6. DIPOLE Power converter
  Current setting in Room:
- CWU, Aux evaporator & main compressor very close
    to allow access to DIPOLE power converter
   (clearing space 600 mm)
 - Main access route some 1,7m
  Placement of water manifolds very close to compressor.
  To close ?! Entry behind compressor inhibited …..
  Installment elsewhere better
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	3
  1,7 m
600 mm
600 mm
600 mm
[Speaker Notes: 3. Adapted design of the Cryogenic apparatus inside Room E40.310 There are 2 new entries inside the cryo-compressor room. The first one, as shown before, is the auxiliary evaporator (here) which is foreseen between the CWU and the main compressor. The other one is this set of pressurized water manifolds (here) which cycles cooling water to main compressor and the DIPOLE Power Converter. We need access to reach all components inside the room, some 600 mm are assumed so this placement of the water manifolds might pose constraints. If this turns out be the case a placement elsewhere is needed. - Which brings me to my next slide -]

---
 4. Alternative placement for water manifolds inside double floor in E40.310
 Option 1 or 2 depending on spatial conditions
 1,3 m height
N
- Placement inside double floor seems better. (No spatial constraints yet inside)
- Space above available for priority installments. (Hoses to be fed through service opening in floor tiles)
- 1,3 m height allowing for maintenance works
- One time installment inside double floor
  No maintenance works needed once securely fixed and tightened.
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	4
[Speaker Notes: 4. Alternative placement for the water manifolds inside the double floor of the compressor room Placement of the manifolds inside the double floor can be a good alternative. There’s space available so the room above can be used for priority installation of the cryogenic components. Access and return hoses to the consumers can be routed through the floor tiles by way of a service opening. The 1,3 m in height allow for necessary operational freedom for installation. So once the connection to the manifolds are secured and tightened no maintenance is required any more. - Which brings me to my next slide -]

---
 5. Conduit entering and leaving Room E40.310 to the maintenance area
 Routing through double floor
3
Departing in Level E.30 towards E10.201
Routing of HE & N2-Lines
1. N2 Line from HE Shield Cooling Cycle (DN20, 15m, not isolated)
2. N2 Line to valve Terminal E10.103 (DN20, 130m, not isolated)
3. HE-Line to Control dewar (Transferline, isolated) 65m
- All conduit entering the hall via room E40.310.
- lines leaving through double floor in E.30 below main
  truck opening
  Less spatial constraints than routing in E.40
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	5
 From He-Shield cycle
 Room E40.310
[Speaker Notes: 5. Conduit entering and leaving the Cryo compresor room Regarding the gasline routing the following has changed: All gasline conduit enters room E40.310 directly from north and connects the consumers through the inside of the hall. The lines are routed in the double floor in level E.30 to keep them below the truck opening in E.40. There are less spatial constraints inside level E.30]

---
 6. He-Line (de)coupling to/from Control Dewar - possible issues -
Picture courtesy by Marion Kauschke, Cryo Dpt.
Rigid He-line arriving via 90 degree elbow from north.
Structural elements for pipe allow no tolerances in positioning.
Any coupling under load will lead to bending stress in 90° elbow.
 Degrees of freedom up- & downstream needed to couple line
 without constraints
- Helium may blow off
- damage to VCR Connection ?
Can flexible connection hoses be used instead of proposed rigid line by BINP ?
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	6
 Stress imposed on isolation & material to be avoided
 4,6 m length
[Speaker Notes: 6. Helium line attachment to control dewar -possible issues- I would like to bring up a possible issue regarding any coupling and decoupling procedures between the Helium line and the Control Dewar. The actual He-Line arrives via an 90° bend. To avoid any forced coupling to the control dewar, tolerances in position of the magnet have to be outbalanced. Structural elements do not allow movements of the HE-Line. It is a rigid pipeline. The question is: Can flexible hoses be used to connect to the Control Dewar to avoid any mechanical stress imposed to the pipeline ? -This brings me to the adaptions inside the MVD-Pit-]

---
2. Adaptions inside MVD-Pit
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	7

---
8. Situation inside MVD-Pit - Assumptions and Iterations -
        N
Information and question received from
Lennart Ahrens.
- isolation cover for EMC assumed with
  with bigger ø 0,3m + tank = 1,3 m
- extra line for supply of dry air inside tank
  isolation asked for.
>>…. Der Tank wird also vom Durchmesser noch ein wenig größer werden, momentan schätze ich ca. 20-30 cm mehr Durchmesser. Genau kann ich das aber erst absehen, wenn der Tank hier ist ….
… da es vermutlich schwierig wird, den Tank komplett Luft-und Feuchtigkeitsdicht eingepackt zu bekommen, denken wir über das Einleiten trockener Luft unter die Isolierung nach. Die müsste natürlich irgendwo herkommen, und daher wollte ich fragen, ob überhaupt die Möglichkeit bestünde, dafür eine Leitung in den Pit zu legen ? …. <<
3
Remark: Where to get a continuous stream of dry air from ?
        No plans to employ an air compressor or turbine (lack of space & costly) !
Question: How can condensation be avoided short of using an extra air compressor ?
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	26.10.2021	8
 Ø 1,3 m ?
 Leakless Rack cooling reservoir: ø 2m
MVD components:
Changes of design
ongoing ?
EMC
[Speaker Notes: 8. Space situation inside the MVD-Pit There is an open issue with additional space asked for the EMC reservoir. Firstly there are plans to cover the reservoir with an insulation. This need some additional 300 mm in diameter. Secondly dry air is planned to be shuffled inside the insulation of the tank. This requires an additional line inside the pit. The question is where to get a continuous stream of dry air from. We have no plans to engage any air compressor. So how else can the insulation issue be solved ?]

---
 7. Access routing to area E10.201
Topics to clarify:
Consultation with the cryodepartment regarding flexible He-Line
connection to the Dewar.
No (dry) air compressor installation to be planned inside the hall.
How else can the condensation problem be solved ?
Space requirements for the EMC tank depending on the status of
MVD Components. The smaller the better.
What is the developmental state of the MVD Cooling parts in the pit ?
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	15.06.2021	9
[Speaker Notes: 8. Topics to be clarified: There’s consultation needed with the Cryogenic department regarding the flexible attachment of the Helium line. Regarding the insulation for the EMC reservoir we do not know if we have 300 mm surplus available in the pit. Apart from that we do not intend to employ an air compressor or turbine in the hall. How can this problem be solved otherwise ? Also space requirements for the EMC reservoir depend on the status of the MVD parts. So the question is: What is the developmental status of the MVD-Components ?]

---
        Thank you for your attention
GSI Helmholzzentrum für Schwerionenforschung PANDA	Daniel Glaab	09.03.2021	10
[Speaker Notes: Tank you for your attention]