## Slide 1
Technical Building Infrastructure Commissioning
Strategy, Phases, Timeline & Status
07.11.2024
B. Redmer
FAIR Site & Buildings

## Slide 2
TOP 1: Commissioning Concept
TOP 2: Commissioning Strategy
TOP 3: Schedule and Status
Content
Notes: 1

## Slide 3
H0719A
K0720A
L0516A
L0409A
L0321A
K0314A
K0519A
G0702A
K0308A
K0410A
K0321A
K0406A
K0619A
K0923A
K0503A
beam line / utility distribution full configuration FS
utility supply full configuration FS
utility supply reduced configuration FS
beamline
K0617A
L0317A
Optionsgebäude
L0608A
Optionsgebäude
H0705A
G0704A
TOP 1 Commissioning Concept
Overall Operation Concept
Notes: 2

## Slide 4
The complexity of the technical facilities requires a
systematic approach while scheduling the commissioning activities.
The picture shows the systematic dependencies between the different technical facilities.
The entire configuration consists of approx. 3.000 technical facilities combining approx. 107.000 technical components.
TOP 1 Commissioning Concept
Notes: HTML und PDF mit einbinden.

## Slide 5
PDB = Planning Database FSB
CDB = Components Database Owner
Power Supply
Building Automation
Heating / Cooling
Customer Equipment
Interface matrix PDB-CDB (TGA - Customer)
Example T1S1MH01 (magnet with power supply and rack)
TOP 1 Commissioning Concept

## Slide 6
The commissioning process of each technical facility consists of 7 phases:
Design
Construction
Construction verification
Internal commissioning
Integrated commissioining
Plant-wide commissioing and testing (approval)
Start-up and operation
TOP 1 Commissioning Concept
Process
Notes: 5

## Slide 7
I
II
III
IV
V
VI
VII
FSB Commissioning Management
Contractor
Design, Construction, Commissioning
Technical Experts
(design/construction)
Technical Experts and Authorities
(tests and acceptance)
Fire Safety
(Design)
Fire Safety
(during construction and commissioing)
Planner
(LPh1-5)
Planner
(LPh8-9)
Owner
(training und instruction) (turnover and operation)
TOP 1 Commissioning Concept
Responsibilities
The commissioning process of each technical facility consists of 7 phases:
Design
Construction
Construction verification
Internal commissioning
Integrated commissioining
Plant-wide commissioing and testing (approval)
Start-up and operation
Notes: FSB IBN Management führt den Gesamtprozess
6

## Slide 8
TOP 2 Commissioning Strategy
Power Supply

## Slide 9
TOP 2 Commissioning Strategy
Power Supply (General Power)
H0719A
K0314A
UA Nord
PP
UA Süd
AV
K0720A
K0923A
L0608A
H0705A
L0516A
K0308A
L0409A
L0321A
K0406A
K0410A
L0317A
G0704A
G0702A
K0617A
K0619A
K0503A
provisional Link 12/2024
Q2/2025
Q4/2025
Q4/2025

## Slide 10
TOP 2 Commissioning Strategy
Cooling Water

## Slide 11
TOP 2 Commissioning Strategy
Cooling Water (25/45)
H0719A
K0314A
K0720A
K0923A
H0705A
L0516A
K0308A
L0321A
K0406A
K0410A
L0317A
G0704A
G0702A
K0617A
K0619A
K0503A
Q1/2025
K0519A (P1)
K0519A (H)
K0519A (G)
Q4/2025
Q4/2025
Q1/2025
Q1/2025

## Slide 12
Utility
2024 | 2025 | 2026 | 2027
Cryo
Power
HEBT
SIS100
Provisional link from transformer substation south to H0719A (AV)
Provisional power supply for K0720A
S-FRS
Cooling water supply for Cryogenic plant testing and commissioing
Permament link transformer sub-station north to H0719A
(PP)
Permanent link transformer substation south to H0719A and K0314A
(AV)
Power supply for HEBT component testing in G0702A, H0705A, K0617A
Power supply for SIS100 component testing
Power supply for S-FRS component testing in L0516A
Cooling water and instrument air for Cryogenic plant
Utility supply for S-FRS component testing in L0516A
Utility supply for SIS100 component testing
Utility supply for HEBT component testing in G0702A, H0705A, K0617A
Construction / Commissioning HBO Operations
TOP 3 Schedule and Status
3.1 Interface Milestone Overview
 | IV | I | II | III | IV | I | II | III | IV | I | II | III | IV
u
v
w
x
y
Notes: HBO Abnahme und Regelbetrieb als nächste Folie.

## Slide 13
TOP 3 Schedule and Status
3.2 Detailed Schedule based on Commissioing Concept
Der Weg von Einzelanlagen zu einer Gesamtanlage
wird durch das Gewerkeübergreifende IBN Konzept
sichergestellt.
Notes: HBO Abnahme und Regelbetrieb als nächste Folie.

## Slide 14
TOP 3 Schedule and Status
3.3 Detailed Schedule based on Commissioing Concept
Example G0704A HEBT supply building
Notes: HBO Abnahme und Regelbetrieb als nächste Folie.