## Slide 1: SIS100 Main Power Converters Status of the installation with outlook on the commissioning
V. Plyusnin
4th SIS100 Workshop: Procurement and Installation

## Slide 2: Content
  SIS100 Main Power Converters
    Overview and production status
    Installation status
    Outlook on the comissioning

## Slide 3: SIS100 Main Power Converters
Overview and production status
Main Dipole PC: 2 power units (PU) in series + quench protection (12 DCCBs + Rds) Iout = 13200 A di/dt = 19 kA/s Vout = ±1400 V Pmax = ±18,5MW Sn = 12 MVA | (2x) Main Quadrupole PCs: 1 power unit + quench protection (4 DCCBs + Rds) Iout = 8500 A di/dt = 15 kA/s Vout = ±700 V Pmax = ±6MW Sn = 4 MVA

## Slide 4
AC-DC
DC-DC
SIS100 Main Power Converters
Overview and production status
Notes: Elektroinstallationen fehlen noch

## Slide 5: SIS100 Main Power Converters
4 T/s operation – 14.5/11.5 kA
Water-cooled
DCCT heads ready
Overview and production status

## Slide 6: SIS100 Main Power Converters
In total components to be installed:
  U10:
    8 x 20kV Switchgear Cabinets
    10 x 20kV/400V Transformers
  U20:
    Main Supply Building (S4):
      20 x AC/DC Converters
      12 x DCCBs
      3 x Crowbar Cabinets
      3 x DCCT Cabinets
      WC-Bus-bars
      8 x Mechanical Switches (Nische 5)
      WC-Bus-bars (Nische 5)
    Auxiliary Building (S3):
      4 x DCCBs
      WC-Bus-bars
      2 x Mechanical Switches (Nische 3)
      WC-Bus-bars (Nische 3)
    Auxiliary Building (S1):
      4 x DCCBs
      WC-Bus-bars (Nische 1)
      2 x Mechanical Switches
      WC-Bus-bars (Nische 1)
Installed
Notes: alle geräte auser für den teststand sind bereits unten, DCCBs mit aufzug einbgebracht in B3 und B1, futterbläche, kein gabelstpler im bereich erlaubt

## Slide 7: SIS100 Main Power Converters
U20: Main Supply Building (S4)
1
QD
1
Dipole
1
QF(1+2)
Most of the main components are already stored in U20 using main crane and cabinet transport trolley
Installation is ongoing using portal crane and forklifters
Some components still at Testbench in Berlin
Electrical installation works are under preparation (U10+U20) as well as water cooling infrastructure
Notes: How to interconnect?

## Slide 8: SIS100 Main Power Converters
U20: Installation Concept
1
1
2
2
2
3
3
3
4
4
4
5
5
6
Installed
Installed
Build
Build
Build
Build
Build
Build

## Slide 9: SIS100 Main Power Converters

## Slide 10: SIS100 Main Power Converters
Dipole:
Production - WC-Busbars:
Q1/2026
Notes: 3-4 month after order.

## Slide 11: SIS100 Main Power Converters
Niches 5, 3, 1:
8 x MS
WC-busbars 2
All Mechanical Switches were successfully installed using mini-crane and hand fork-lifters
Next steps:
  Bus-bars to connect the CLBs (still missing info. from GSI!)
  Electrical installations and grounding of the components
  Installation of the control and pulling of the control cabling
  Installation and connection of the water distributions
  Connections of F1 and F2 magnet systems ins series for the FQuads.
Notes:   Discussions how to bring the Switches to the platform.

## Slide 12: SIS100 Main Power Converters
All DCCBs were inserted using elevators and cabinet transport trolley
All DCCBs installed using forklifters and appropriate supporting wood constructions
Dump resistors were installed on the top of the cabinets with chain hoists
DCCB Rooms U20 – 322/222
Next steps:
  Output Bus-bars transport and installation
  Electrical installations and grounding of the components
  Installation and pulling of the control cabling
  Installation and connection of the water distributions

## Slide 13: SIS100 Main Power Converters
Further installation activities:
Upcoming installation of the rest of main components:
Notes: Detailed Installation Concept U20 – 500 entries

## Slide 14: SIS100 Main Power Converters
Routine tests
  Isolation tests
  Pressure tests
  Thermal test with full current of the inverters
Operation of two converters in series (DC & ramped modes) completed
  Current flow in both directions
  Accuracy tests on a test load
Operation mode of two converters in parallel (DC & ramped modes)
  Operation and accuracy tests
  With reactive power compensation of SIS18 current shape tested
Safety concept being finalized based on test results
  MPS Trigger
  Performance of the system safety mechanisms
FAT of 2xFoS Inverters – Done Q4/2023
System Safety Test – Done Q4/2024
Notes: Installation

## Slide 15: SIS100 Main Power Converters
Commissioning of the main power converters:
  SAT Aa - End of installation including VDE tests, pressure tests, etc.
    Pre-conditions: 400V supply
  SAT Ab:
    Dry commissioning without 20 kV [i.e. signal checks, functionality tests without power, etc.]
      Pre-conditions: Cooling water available, output power cables connected and tested
    Short circuit test with 20kV [i.e. operation of the complete power converters]
      Pre-conditions: 20kV supply, doors with locks and working emergency-off system.
  SAT B – Supply of the final load
    Pre-conditions:

## Slide 16: SIS100 Main Power Converters
SAT Ab:
SAT B:

## Slide 17
Thank you for your attention