## Slide 1: Bi-Phase CO2 cooling of the CBM Silicon Tracking System (STS) detector
Evgeny Lavrik1, Anton Lymanets2, Jorge Sanchez Rosado2, Hans Rudolf Schmidt1,
1Eberhard Karls Universität Tübingen, 2GSI Darmstadt
Mathematisch-Naturwissenschaftliche Fakultät
Cooling Challenges
To avoid thermal runaway the silicon sensors have to be kept at -5˚C. This is quite challenging as about 50 kW of heat is dissipated from the STS Front-End-Boards (FEB) and Read-Out-Boards (ROB) into a rather small volume with very limited space for heat exchanger plates. We use bi-phase CO2 cooling due to its superior volumetric heat transfer coefficient, which is about an order of magnitude better than conventional freons.
Within this project we have:
built an open CO2 cooling system for testing heat exchanger efficiencies;
tested different designs of FEB box and measured the temperature distribution when attached to a heat exchanger;
compared with Solid Works FEM simulations;
built a sophisticated 1 kW closed CO2 system (TRACI XL);
TRACI XL will be used to test a quarter station with heat load of up to 1 kW.
FEB-Box and ROB-Box cooling R&D
Open Blown CO2 cooling system
simple layout and control
allows basic tests of CO2 cooling efficiencies of different heat exchanger designs
FEM Calculations of Temperature Distribution
R&D results
Power Applied, W | Maximum temperature, °C |  | 
 | 1mm | 2mm | 3mm
140 W | 15 | -14.2 | -22.6
200 W | 24 | 0.2 | -15
TRACI-XL, a 1 kW CO2 Cooling Plant
The cooling plant is fully controlled by a standard PLC Siemens S1200.
TRAXI XL provides liquid CO2 in the temperature range from -40⁰C to 5⁰C at the bi-phase boundary. The diagram shows two possible thermodynamical cyles, the latent heat will be used in the heat exchanger for cooling up to 50% vapor quality.
3mm FEB-box design is sufficient to completely remove the heat from the front-end electronics.
Simulated 1mm ROB-box design already allows to keep the read out electronics at -11 ⁰ C.
Solidworks based temperature simulations of FEB-box (left) and ROB-box (right);
allows to experiment and fine-tune parameters;
evaluation of cooling for front-end boards for different shelve thicknesses;
Traci XL will be used to test the cooling efficiency of a 1 kW quarter station cooling demonstrator. Heat exchangers (in blue) take the thermal load form the front-end electronics. The left side figure shows the channels for the liquid CO2 flow in the heat exchanger; the right side figure show the cooling plate with shelves for the front end boards attached.
The CO2 gas-liquid mixture is re-liquefied in a
condensing unit which uses R404A (freon) as secondary coolant at a minimum temperature of -45⁰C in the low pressure side.
Maximum temperature, °C |  | 
T, coolant | T@200W | T@140W
-40 | -10.6 | -12.7
-30 | -4.9 | -9.9
-20 | 0.8 | -4.1
-10 | 6.5 | 1.58
Experimentally measured maximal temperature on the FEB box in dependence of power applied and shelve thickness
Result of simulations showing the expected maximal temperature on the FEB box in dependence of initial coolant temperature and power applied