## Slide 1
The Barrel’s Cooling System Status

## Slide 2
The Slice cooling system (J. Xu and Christine)
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem
The cooling system for the Barrel (Y. Guarnelli, Philippe and Christine)
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)
The cooling machine (M. Josselin, Tobias, C. Thaï and Philippe)
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical problem

## Slide 3
The Slice cooling system (J. Xu and Christine)
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem
The cooling system for the Barrel (Y. Guarnelli, Philippe and Christine)
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)
The cooling machine (M. Josselin, Tobias, C. Thaï and Philippe)
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical problem

## Slide 4
Barrel
1 Slice
16 Slices
Crystals temperature = -25°C

Each Slice need a cooling system and an insulation
Upstream Ring
Crystals
Support Beam
The cooling system principle
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 5
Old cooling system
Upper cooling system
Lower cooling system
The cooling system principle
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem
-25°C
+20°C
+20°C
Upper cooling system
Lower cooling system
26mm
50mm
Back side
Front side

## Slide 6
Total pressure drop with Water Methanol for 16 Slices = ~ 230 mbar for ± 0.1°C
3 brass Manifolds
Upper cooling system =
2 copper rectangular pipes (10x20mm2)+ 1 copper plate
Dv= 24 l/mn
Lower cooling system =
10 Polyurethane circular pipes f 6x4 +
a composite sandwich
Dv= 3.5 l/mn
Copper and Brass forbidden
Old cooling system for a working temperature of -25°C ± 0.1°C
The upper cooling system’s change
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 7
Upper cooling system =
3 PU pipes f 8x6
Dv= 4 l/mn
Lower cooling system =
10 PU pipes f 5.5x3.5
Dv= 0.75 l/mn
4 stainless steel manifolds
Total pressure drop with Water Methanol for 16 Slices = ~ 630 mbar ± 0.3°C
Composed of Polyurethane (PU) circular pipes
fixed on the Back Plates with small pipes
and plates made in Stainless steel
The upper cooling system’s change
New cooling system for a working temperature of -25°C ± 0.3°C
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 8
VIP (Vacuum Insulation Plate) Part (VAQTEC®)
PU Pipes
Plastic support
Carbon foil
The front insulation system :
the principle = composite sandwich technology
Aluminium foil
Proto120 technology
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 9
The front Insulation system :
the principle = composite sandwich technology
VIP ”bending” Plate
Aluminium foil
Carbon plate
Filling foam part
Epoxy fixation part
Shapes for the PU pipes
26mm
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 10
Δ=0.0013mm
Δ=0.45mm
Δ=0.035mm
~ 2400 mm
The front insulation system :
the calculations made with Ansys
D
Best deflection
Easier to seal the enclosure for the nitrogen
First calculus = 1 Slice
Second calculus = 4 Slices
Third calculus = 16 Slices
Shell calculus
Fixations on the edges
q = total distributed load (water methanol + pipes + sandwich)
Equivalent Young Modulus for the 4 materials
All the calculi are based on an equivalent Young Modulus Composite structure = Carbon + VIP + Foam + Aluminium glued together
Need to make some tests with this composite structure to measure the “real” Young Modulus
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 11
Fixation on the Downstream Ring
The front insulation system :
the last shape
Services outlets ??
No design on the Upstream Side
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem

## Slide 12
The Slice cooling system
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem
The upper cooling system’s change
Power in the Support Beam created by the electronic = 300 W
Need to have pipes with water (Dv 0.4 l/mn) in the Support Beam in order to :
  have cool water to prevent the reheating of the Support Beam when its electronic is on
  Have hot water to prevent a big cooling in the Support beam when its electronic is off
Temperature chart of the Support Beam
The dew point problem
The Dirc and the Crystals = very closed
Need to have heating resistance in order to prevent the creation of ice between these two systems :
Power of 11.25 W/m2
  Resistance = 51
    Intensity = 470mA
Use kapton heating resistance with a thickness  0.15 mm

## Slide 13
The Slice cooling system (J. Xu and Christine)
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem
The cooling system for the Barrel (Y. Guarnelli, Philippe and Christine)
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)
The cooling machine (M. Josselin, Tobias, C. Thaï and Philippe)
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical problem

## Slide 14
The pipes insulation
20 m
2 Outlets
2 Inlets
D(outlet) int = 38 mm
D(inlet) int = 16.7mm
L = 90 mm
Best insulation
The principle :
Pomp
Connection Pipes
(Box?)
The cooling system for the Barrel
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)

## Slide 15
Total power drop = 16.6 W/m
For Water Methanol :
Total temperature drop = 0.001°C/m
Total power drop = 1.93 W/m
For Water Methanol
Total temperature drop= 0.0001°C/m
Styrofoam
2 Stainless steel pipes
Vacuum
2 Stainless steel pipes with super insulation material
Epoxy shim
Solution 1 :
Solution 2 :
Insulating jacket
The best solution :
Power drop for 20m  330 W
Temperature drop for 20m  0.023°C
Easier to do
Cheaper
The pipes insulation :
The cooling system for the Barrel
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)

## Slide 16
The cooling system for the Barrel
  The principle
  The pipes insulation
  The installation in the Panda hall
  The pressure requirement (pressure drop study)
The installation in the Panda Hall :
How to disconnect and connect easily?
Working position
Services position

## Slide 17
The cooling system for the Barrel
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)
Telescopic pipes
Flexible pipes
Double circuit
Bleeder & drain valve
Bleeder & drain valve
Pomp
Chiller
Three solutions
The installation in the Panda Hall :
Working position
Services position

## Slide 18
The pressure requirements :
-25°C
P > 0.2 bar (Leak less method)
Pressure drop Outlet ?
P< 3 bars (Characteristics of the machine)
Pressure drop Inlet ?
Pressure drop due to the gravity ?
Z =+ 4.3 m
Z =+ 3.55m
Z =+ 2.8 m
Z = -2 m
Pressure drop in the slice ?
The cooling system for the Barrel
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)

## Slide 19
Bernoulli equation
Change in kinetic energy
Change in gravitational potential energy
Change in potential pressure energy
Pressure drop
Exchange energy between the coolant and the machine
The Pomp-Slice way :
The Slice-Pomp way :
The cooling system for the Barrel
  The pipes insulation
  The installation in the Panda hall
  The pressure requirement (pressure drop study)
The pressure requirements :

## Slide 20
Z =+ 4.3 m
Z =+ 3.55 m
Z =+ 2.8 m
Z = -2 m
DJpompe inlet= +0.08 bar
DJchiller = +0.67 bar
DJmanifold inlet= +0.02 bar
DE’p chiller-slice = +0.44 bar
DJxxx = linear pressure drop
DE’p= gravitational potential energy drop
DJmanifold outlet = -0.002 bar
DJpompe outlet = -0.08 bar
DE’p slice-slice = +0.14 bar
DE’p slice-slice = - 0.57 bar
p = 1.21 bar
DJSlice=+0.63 bar
PPomp-Slice = 2 bar
0.2 bar<PPomp-Slice <3 bar
OK
PSlice-Pomp = 1.35 bar
DJxxx = singular pressure drop
The cooling system for the Barrel
  The pipes insulation
  The installation in the Panda hall
  The pressure requirement (pressure drop study)
The pressure requirements :

## Slide 21
The Slice cooling system (J. Xu and Christine)
  The cooling system’s principle
  The upper cooling system’s change
  The front insulation system
  The dew point problem
The cooling system for the Barrel (Y. Guarnelli, Philippe and Christine)
  The principle
  The pipes insulation
  The installation in the Panda Hall
  The pressure requirement (pressure drop study)
The cooling machine (M. Josselin, Tobias, C. Thaï and Philippe)
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical hitch

## Slide 22
Chiller
Skid
(for Orsay or without external cooled water)
Pump
Aerocooler
(for Orsay or without external cooled water)
380 V 16 A
380 V 16 A
Flowmeter
1,5kW heater
220 V
Pump ON
Remote control
Emergency ON/OFF
CROUZET
ECAL detector
Computer
Vacuum pump
220 V
External water in Giessen
EMC Temperatures -25°C
Temp. EMC inlet
(security -40°C)
RS485 connection
Water methanol exhaust
Nitrogen bottle
Set °C
Real °C
Set °C
EMC °C
EMC inlet °C
380 V 32 A
Control panel
(Distribution box?)
ON/OFF
ON/OFF
25m
15m
15m
Temperatures EMC + Inlet EMC (4-20mA)
5m
Manometer
  The Installation schematic of the cooling machine:
Arrival at Orsay end of 2014
Running check with water at 16°C
The housing box and tubes connections were made in January
The cooling machine
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical accident

## Slide 23
Chiller
Skid
(for Orsay or without external cooled water)
Pump
Aerocooler
(for Orsay or without external cooled water)
Flowmeter
1,5kW heater
Pump ON
Remote control
Emergency ON/OFF
CROUZET
ECAL detector
Vacuum pump
Set °C
Real °C
Internal view
Internal view
Pump circulator of the chiller
Electromagnetic flowmeter
Some pictures
The cooling machine
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical problem
  The Installation schematic of the cooling machine:

## Slide 24
The control panel is done on a PC with Labview (compatible with EPICS used by Bochum)
The cooling machine
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical problem
  The Installation schematic of the cooling machine:

## Slide 25
Chiller
Skid
(for Orsay or without external cooled water)
Pump
Aerocooler
(for Orsay or without external cooled water)
Flowmeter
1,5kW heater
Pump ON
Remote control
Emergency ON/OFF
CROUZET
ECAL detector
Computer
Vacuum pump
EMC Temperatures -25°C
Temp. EMC inlet
(security -40°C)
RS485 connection
Set °C
Real °C
Set °C
EMC °C
EMC inlet °C
Control panel
(Distribution box?)
ON/OFF
ON/OFF
Manometer
The RS485 connections with the flowmeter and the pump are done
Installation of a security 3 bar valve (chiller over-pressure problem)
But
We can’t read out the electronic manometer (pin-out problem)
We can’t control the Vacuum pump (Grundfos drivers not found yet)
The control command is still to be finished (with Tobias)
Security valve
The cooling machine
  Installation schematic of the cooling machine
  Things done and things to do
  Technical anomalies discovered
  Technical problem
Things done and things to do :

## Slide 26
Chiller
Skid
(for Orsay or without external cooled water)
Pump
Aerocooler
(for Orsay or without external cooled water)
Flowmeter
1,5kW heater
Pump ON
Remote control
Emergency ON/OFF
CROUZET
ECAL detector
Computer
Vacuum pump
EMC Temperatures -25°C
Temp. EMC inlet
(security -40°C)
RS485 connection
Set °C
Real °C
Set °C
EMC °C
EMC inlet °C
Control panel
(Distribution box?)
ON/OFF
ON/OFF
Temperatures EMC + Inlet EMC (4-20mA)
Manometer
Anomalies discovered:
Severe electromagnetic compatibility affected the thermal sensors if not chiller earth connected => the manufacturer gave an anti-parasitic device. We still need to test it
The thermal sensors are very fluctuating. The manufacturer provide a new program to change the channels hub. Looks better but still need to check it.
The hot gas technology to regulate the power is too strong. Need a new program to control it.
Technical anomalies discovered :
The cooling machine
  Installation schematic of the cooling machine
  Things done and to do
  Technical anomalies discovered
  Technical hitch

## Slide 27
Chiller
Skid
(for Orsay or without external cooled water)
Pump
Aerocooler
(for Orsay or without external cooled water)
Flowmeter
1,5kW heater
Pump ON
Remote control
Emergency ON/OFF
CROUZET
ECAL detector
Computer
Vacuum pump
EMC Temperatures -25°C
Temp. EMC inlet
(security -40°C)
RS485 connection
Set °C
Real °C
Set °C
EMC °C
EMC inlet °C
Control panel
(Distribution box?)
ON/OFF
ON/OFF
Manometer
 The heat exchanger exploded locally
and the compressor drank coolant…
Question :
We are working on the water methanol mixture icing risk.
How to control it ?
At -32°C, the chiller will run at -42°C and the mixture must not go down 50% to avoid freezing.
The technical problem :
Due to :
a bad user manual
a lack of security in the ice risk (even with water coolant at 10°C) because the flow meter protection foreseen in the study is not enough
The cooling machine
  Installation schematic of the cooling machine
  Things done and to do
  Technical anomalies discovered
  Technical problem
Consequences :
Repair of the chiller is undergoing …
At the return mid April, the run will be done by the company and we still need to show that we CAN achieve the required stability. (Only two months to do it…)
We expect to do all the tests with glycol water coolant to get a good control on the ice protection (instant reading with refractometer)

## Slide 28
  For the Slices :
      Test a sample sandwich to know the real Young Modulus of the Front insulation system
      The Upstream front insulation and its fixation
      Integration of the Front Heating resistances
      Integration of the Support Beams cooling system
      Integration of the other services (cables, pipes and optic fibers)
  For the Barrel :
      The final design of the pipes, the Manifold box and the double circuit in the Panda Hall
      The pipes connection between the Slices and the Manifold box(the distribution pipes for the Barrel)
  For the Cooling machine :
      Test the anti-parasitic device and the new program to change the channels hub for the thermal sensors at Orsay
      Read the electronic manometer and control the Vacuum pomp with the control command at Orsay
      Be able to achieve the required stability at Orsay
      Install the cooling machine and test it at Giessen
      Finish the control command (Tobias)
      ...
To do or to finish:
??
Orsay
+
Giessen
+
Bochum
Reminder:
IPN Orsay has officially stopped its activities on Panda since last June.
At the end of August 2015, no more technical contribution from Orsay.

## Slide 29
Thank you for your attention