## Slide 1: Towards an EPICS based Detector Control System for the CBM Micro Vertex Detector
Philipp Klaus & Ole Artz for the CBM-MVD Collaboration
26 February 2018, DPG-Verhandlungen 2018 in Bochum

## Slide 2: Tasks of Control Systems
Monitoring
Visualization
Archiving
Tracing (protocolling access)
Control (manual or automatic)
Alarming / Alerting
EPICS: Experimental Physics and Industrial Control System
→ our system, covered in this talk
Be it in an industrial setting like a production plant or…
a large physics experiment
Intro
Notes: It should aggregate information from all sub systems for a wholistic view of the system status.

## Slide 3: EPICS for the CBM-MVD (PRESTO)
What is PRESTO? → The most sophisticated prototype of the Micro Vertex Detector we have:
  Mimosa-26 based (= legacy read-out)
  15 sensors integrated one one quadrant made from TPG
  Realistic heat dissipation (>= heat dissipation of final sensor MIMOSIS)
  Successfully tested (=operated) in vacuum chamber
Goal: Confidently run the system 24/7 in the laboratory to identify potential problems and to test the control system.
Vacuum
55F
PRESTO
PRESTO: Prototype of the MVD-station #2 quadrant
Intro

## Slide 4: The Protocol Behind EPICS: Channel Access
The basic verbs for a channel access client:
  caget
  caput
  camonitor
Highly scalable for large real-time systems: upon connecting to the IOCs, (long) PV names are mapped to numerical channel IDs → improves latency and throughput
http://www.aps.anl.gov/epics/docs/APS2014/05-CA-Concepts.pdf
Request status of a control variable
Update value of a control variable
Subscribe to changes of a control variable
The “backbone” of EPICS
Intro

## Slide 5: EPICS Terminology
Channel Access (CA) The communication protocol used by EPICS
Process Variable (PV) A named endpoint of readable or writable information in channel access
Channel Access Server (CAS) Server software to provide PVs via CA on the network
Channel Access Client (CAC) A consumer of / controller for the offered data
I/O Controller (IOC) A channel access server with many modules to realize device communication, setting limits, alarms, and more.
Intro

## Slide 6: Timeline Detector Control System (DCS) for the CBM-MVD
MVD Prototypes
(mMVD / mCBM)?
PRESTO to
run 24/7
with DCS
MVD
at CBM
Implementation of many Devices (IOCs)
(2017-04 - current)
CSS Archiver deployed w/
PostgreSQL
(2017-07)
Div. tools emerged to ease usage & development
(ongoing)
Current Situation
Alarm Handling
Sequences
/ FSMs
Intro

## Slide 7: Areas of Control
Environmental
  Lab temperature
  humidity
Powering
  Low voltage power supplies
  voltmeters
Safety
  Hardware interlocks,
  Latch-up protection
  Emergency Shutdown
Vacuum
  Pressure Gauges
  Valves
Cooling
  Cooling Plant
    Setpoint
    Circulation
  Sensor Temperature
→
Not all aspects can be covered by EPICS, employing a DCS is rather wholistic, means more than just deploying one piece of software.
Control
  Steering
  Automation
Intro

## Slide 8: Device Overview
Category | Vendor & Product | Type of Interface | Support
Bench Power Supply | Hameg (now R&S) HMP 4030 / 4040 | USB (FTDI) | ✓
Bench Power Supply | Hameg (now R&S) HMC 8043 | USBTMC / VXI-11 | ✓
Cooling System | Huber CC-405 | RS-232 | ✓
Vacuum Gauge Controller | Vacom MVC-3 | RS-232 | ✓
Vacuum Gauge Controller | Balzers PKG 020 | Analog Vout | ✓
General Purpose ADC | ADCuC Board (IKF development) | USB Serial | ✓
Cooling: Flow Meter | Kobold DPM (ATmega 32u4 uC) | USB Serial | ✓
Temperature Sensors | Pt100 IKF 8ch board (ATmega 328p) | USB Serial | ✓
Humidity Sensor | Lufft OPUS 20 | TCP/IP | ✓
6½ Digit Multimeter | Agilent 34411A | VXI-11 | ✓
DAQ bridge | TRB3 / trbnet registers | trbnet | 🚧
Meta: Alarm Handling | Soft IOCs | - | 🚧
✓ implemented / finished
🚧 currently being implemented / planned
Via reverse- engineering with 3-way RS232 cable
with
PCASpy
Device Support
Notes: CC-405: ✓ extended support
Pt100: 🚧 extended support

## Slide 9: Device Overview: Outlook
Category | Vendor & Product | Type of Interface | Support
Probe Station | Suess PA200 (Semi-automatic) | TCP/IP | 🚧
Heating/Drying Oven | Memmert UNE 400 | RS-232 | 🚧
🚧 currently being implemented / planned
Via reverse-engineering with Wireshark
Via reverse-engineering with 3-way RS232 cable
Device Support

## Slide 10: Input Output Controller (IOC) Deployment
IOC: The backend controlling EPICS process variables
Currently our IOCs are mostly deployed on a Raspberry Pi 3 single board computer (SBC).
The system is rather “fail-safe”. It runs on a uninterruptible power supply (UPS); hardware interlocks are forseen
All our IOCs are available in a Docker container for fast deployment
Device Support

## Slide 11: Deployment of the CS-Studio Archiver
Database Engine used: PostgreSQL
  “Partitioning” is an important feature helping with:
    fast queries,
    periodic backups,
    scalability.
  We set up partitioning to cover one week per partition.
Archiver

## Slide 12: Implemented User Interfaces
CS-Studio
  For full-fledged system control
  Locally accessible (read/write access)
Web GUI
  Dashboard-like
  For quick status information
  Remotely accessible (read-only!)
  “Mobile First” Approach
User Interfaces
**Check it out for yourself**
https://presto.site

## Slide 13: Website with Live-Data from EPICS CA
Based on the following technology:
Python (main programming language)
PyEPICS (EPICS/CA bindings for Python)
Bottle (micro web-framework)
Furthermore:
  Bootstrap (Responsive, mobile-first layout)
  Jinja2 (template engine)
  d3 (JS visualization toolkit)
PyEPICS
d3.js
Web Dashboard
Bootstrap
**Check it out for yourself**
https://presto.site

## Slide 14: Real-Time Information on Web Interfaces
(Obvious) Technology Choice: HTML/CSS/JS
For real-time applications there are multiple options:
  (HTML refresh meta tag)
  Polling (AJAX)
  Long-Polling (AJAX)
  Publish/Subscribe (WebSockets)
Web Dashboard

## Slide 15: Real-Time Information on Web Interfaces
(HTML refresh meta tag)
Polling (AJAX)
Long-Polling (AJAX)
Publish/Subscribe (WebSockets)
“gview”
“pv list”
Current implementation
Considered for entire web dashboard
Web Dashboard

## Slide 16: Bonus Feature in the Web Dashboard: Graphical Views (“Gview”)
Heartbeat indicating live-status
PV values update
in real-time
Basis: SVG vector image (Inkscape)
Web Dashboard

## Slide 17: CaRecPlay – Channel Access Recording & Playback
In the course of the recent EPICS DCS development, a new tool for EPICS/Channel Access was conceived and implemented by us: CaRecPlay
Consists of two Python scripts:
  carec.py Allows to monitor a given list of process variables via Channel Access → stores the received value updates in a persistance file (.pickle).
  caplay.py Mock-up IOC that can play-back recorded process variables (pretending it would be the device offering those PVs).
Why:
  Safe testing of new features without endangering expensive lab equipment.
  To demonstrate & develop the DCS in a country with filtered Internet.
Tools

## Slide 18: Alarms using data from different devices (IOCs) = ”Meta”-Alarms
Cooling: Off
Power Supply for Sensors: ON
Alarm: Potentially Hazardous Mode
or:
DAQ Switch Port Counter: < 2Mbit/s
Data Taking: ON
Alarm: Malfunctioning Readout
To be detailed.
Alarms
&&
&&

## Slide 19: Summary Of Our EPICS DCS Developments
DAQ / trbnet Support
Plotting Webserver for archived values
Device Coverage
Archiver Deployment
CS-Studio Interface
Web Dashboard
  SVG illustrations
  Tabular overview & sparklines
CaRecPlay
Bridge: EPICS CA → MQTT
Realized
Under Development
Upcoming
Sequencing: self-contained state machine within IOC
Alarm Propagation / Global Status
External Alarm Handling: send email, send SMS, flash alarm lights, etc.
Standard EPICS (base)
PyEPICS
CS-Studio
Custom Tool
PCASpy
Thank you for your attention!