## Slide 1: Work Package: PSP 2.5.3.2.1.1. CR Quadrupole magnet Power Converter Type 1
Conceptual Design
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 2
QUAD TYPE | Magnets in series | G kGs/cm | Inom kA | Vm tot V | Vcable V | Vtotal V | Ptotal kW
EWQ | 1 | 0.3 | 1.18 | 33 | 11 | 44 | 52
EWQ | 2 | 0.3 | 1.18 | 66 | 11 | 77 | 91
WQ | 4 | 0.32 | 1.00 | 114 | 10 | 124 | 124
WQ | 4 | 0.32 | 1.00 | 114 | 10 | 124 | 124
WQ | 4 | 0.41 | 1.28 | 144 | 13 | 157 | 201
WQ | 2 | 0.35 | 1.10 | 62 | 11 | 73 | 80
SWQ | 4 | 0.36 | 1.13 | 106 | 11 | 117 | 132
SWQ | 4 | 0.33 | 1.04 | 98 | 10 | 108 | 112
SWQ | 4 | 0.38 | 1.20 | 112 | 12 | 124 | 149
NQ | 2 | 0.43 | 0.83 | 24 | 8 | 32 | 27
NQ | 2 | 0.52 | 1.00 | 28 | 10 | 38 | 38
NQ | 2 | 0.52 | 1.00 | 28 | 10 | 38 | 38
NQ | 2 | 0.43 | 0.83 | 24 | 8 | 32 | 27
NQ | 2 | 0.58 | 1.12 | 32 | 11 | 43 | 48
NQ | 1 | 0.57 | 1.10 | 16 | 11 | 27 | 30
CR Quadrupole Magnets Power Converters Types
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 3
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 4
Power converter type 1 for CR quadrupole magnets technical requirements
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019
Power converter type | CR Quadrupole magnets Power Converter QPC Type 1
Maximum current, Imax | 1500A
Nominal current, IN | 1480A
Range of load current, Imin…Imax | -1500A…1500A
Rise time from 0 to Imax | 5sec
Fall time from Imax to 0 | 5sec
Maximum output voltage Vmax | 200V
ΔIout/ IN | ±50 ppm p-p
Long Term Current Stability | 100 ppm r.m.s.
Operating mode | DC operation, Ramping operation
Control | ACU
DCCT | ACU controlled DCCT
Mains | AC 400V 50Hz TN-S
Maximum Output Power | 300kW
Minimal Power Factor | 0.95
Cooling | Distill Water
Cooling water maximal flow | 16L/min
Cooling water max pressure | 15 bar
Cooling water input temperature | 25°C ± 2°C
Max allowed outlet temperature | 55°C
Load connection cable cross-section | 750mm2
Maximum length of load cable | 200m
Number of cabinets per converter | 3
Power converter dimensions WxDxH, m | 2.75x0.8x2.1

## Slide 5
POWER CONVERTERS LOCATION
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 6
QPC T1 POWER CONVERTERS LOCATION
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 7
POWER CONVERTERS SETUP
High Power part. It is supplied by a 400V, 3-phase Common supply system C2
Control part. It is supplied by a 400V, 3-phase Common supply system C2
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 8: QPC T1 power converter block diagram
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 9: QPC T1 power converter control
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 10: The appearance of QPC T1.
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 11
QPC T1 Grid, water, and load connections
Connection to electrical power : TN-S
Connection to load:
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 12: QPC T1 power control cabinet
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 13: QPC T1 500A power section
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 14: Closed loop simulation
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 15: Closed loop simulation
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019
Step response
Frequency response

## Slide 16: Rectifier simulation
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019
Power factor
Is better than 0.97

## Slide 17: Rectifier simulation
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019
Chart: QPC primary current harmonics
| 0 | 25 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 350 | 375 | 400 | 425 | 450 | 475 | 500 | 525 | 550 | 575 | 600 | 625 | 650 | 675 | 700 | 725 | 750 | 775 | 800 | 825 | 850 | 875 | 900 | 925 | 950 | 975 | 1000 | 1020 | 1050 | 1070 | 1100 | 1120 | 1150 | 1180 | 1200 | 1230 | 1250 | 1270 | 1300
Primary Current | 2.4601e-10 | 2.5399e-09 | 105.9105 | 3.9617e-09 | 2.0927e-09 | 1.5288e-09 | 3.8019e-05 | 8.3387e-10 | 7.9872e-10 | 9.361e-10 | 2.2684 | 3.4345e-10 | 4.5208e-10 | 9.1374e-10 | 1.27 | 3.4824e-10 | 5.7508e-10 | 7.5719e-10 | 4.0415e-05 | 1.1342e-09 | 1.5671e-09 | 2.5559e-09 | 6.3099 | 2.6198e-09 | 3.0351e-10 | 1.0192e-09 | 4.2652 | 3.3706e-09 | 1.5847e-09 | 1.1597e-09 | 2.0927e-05 | 6.4217e-10 | 6.9968e-10 | 9.9201e-10 | 0.6278 | 2.7636e-10 | 5.2556e-10 | 9.8882e-10 | 0.5623 | 2.6038e-10 | 3.099e-10 | 5.2875e-10 | 3.4824e-05 | 3.0671e-10 | 4.8083e-10 | 4.5208e-10 | 0.92812 | 1.5767e-09 | 2.3962e-10 | 4.984e-10 | 0.76997 | 1.9649e-09 | 8.1629e-10
Reference Limits | 0 | 0 | 105.9105 | 0 | 7.2019 | 0 | 11.9679 | 0 | 1.8005 | 0 | 26.4776 | 0 | 0.63546 | 0 | 11.6502 | 0 | 0.42364 | 0 | 1.165 | 0 | 0 | 0 | 7.9433 | 0 | 0.28596 | 0 | 5.8251 | 0 | 0.25419 | 0 | 0.21182 | 0 | 0.21182 | 0 | 3.7069 | 0 | 0.19064 | 0 | 5.8251 | 0 | 0.16946 | 0 | 0.052955 | 0 | 0.14827 | 0 | 1.9064 | 0 | 0.052955 | 0 | 1.5887 | 0 | 0.10591

## Slide 18: QPC T1 Power section simulation
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 19: QPC T1 Production plan
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 20: Thank you for attention
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019