## Slide 1: CR Power Converters
Status
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 2: CR magnet system
CR Magnet System
DC magnets/ correctors
Injection/ Extraction
magnets
24
DIPOLES
40 QUADRUPOLES
6 POWER
CONV
24 SEXTUPOLES
48+12
CORR+OCT
15 POWER
CONV
1 POWER
CONV
48+12 CORR
PS
KICKER
MAGNETS
INJECTION
SEPTUM
EXTRACTION
SEPTUM
INJ SEPTUM PS
EXT SEPTUM PS
KICKER
PSs
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 3: TCR1 magnet system
TCR1 Magnet System
DC magnets/ correctors
2
DIPOLES
6 QUADRUPOLES
2 POWER
CONV
2
SEXTUPOLES
5
CORRECTORS
6 POWER
CONV
2 POWER
CONV
5 CORR
PS
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 4: CR+TCR1 Power Converters
1 CR Dipole magnets Power
Converter
15 CR Quad magnets Power
Converters
2 TCR1 Dipole magnets Power
Converters
6 TCR1 Quad magnets Power
Converters
6 CR Sext magnets Power
Converters
2 TCR1 Sext magnets Power
Converters
12 CR Octupol magnets Power
Converters
48 CR Steer. magnets Power
Converters
7 TCR1 Steer. magnets Power
Converters
1 PC
23 PCs
8 PCs
12 PCs
55 PCs
CR DPC type
CR QPC Type
CR SPC Type
CR OPC Type
CR CPC Type
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 5: CR magnets types
TYPE | SUB | Qty | Imax A | Lm mHn | Rm mOm | Vm V | Deviat
DIPOLES | - | 24 | 1450 | 377 | 62.45 | 91 | 10ppm
QUADRUPOLES | EWQ | 3 | 1500 | 49.8 | 26.31 | 38 | 100ppm
 | WQ | 14 | 1500 | 59 | 26.31 | 38 | 100ppm
 | SWQ | 12 | 1500 | 44 | 21.67 | 31 | 100ppm
 | NQ | 11 | 1450 | 11 | 10.1 | 15 | 100ppm
SEXTUPOLES | - | 24 | 500 | 6 | 35 | 18 | 0.1%
OCTUPOLES | - | 12 | 30 | 86 | 2450 | 74 | 1%
CORRECTORS | H | 24 | 6 | 182 | 9560 | 58 | 1%
 | V | 16 | 14 | 158 | 4200 | 59 | 1%
 | H/V | 8 | 20 | 90 | 760 | 16 | 1%
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 6
QUAD TYPE | Magnets in series | G kGs/cm | Inom kA | Vm tot V | Vcable V | Vtotal V | Ptotal kW
EWQ | 1 | 0.3 | 1.18 | 33 | 11 | 44 | 52
EWQ | 2 | 0.3 | 1.18 | 66 | 11 | 77 | 91
WQ | 4 | 0.32 | 1.00 | 114 | 10 | 124 | 124
WQ | 4 | 0.32 | 1.00 | 114 | 10 | 124 | 124
WQ | 4 | 0.41 | 1.28 | 144 | 13 | 157 | 201
WQ | 2 | 0.35 | 1.10 | 62 | 11 | 73 | 80
SWQ | 4 | 0.36 | 1.13 | 106 | 11 | 117 | 132
SWQ | 4 | 0.33 | 1.04 | 98 | 10 | 108 | 112
SWQ | 4 | 0.38 | 1.20 | 112 | 12 | 124 | 149
NQ | 2 | 0.43 | 0.83 | 24 | 8 | 32 | 27
NQ | 2 | 0.52 | 1.00 | 28 | 10 | 38 | 38
NQ | 2 | 0.52 | 1.00 | 28 | 10 | 38 | 38
NQ | 2 | 0.43 | 0.83 | 24 | 8 | 32 | 27
NQ | 2 | 0.58 | 1.12 | 32 | 11 | 43 | 48
NQ | 1 | 0.57 | 1.10 | 16 | 11 | 27 | 30
CR Quadrupole Magnets Power Converters Types
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 7
QUAD TYPE | Magnets in series | G kGs/cm | Inom kA | Vm tot V | Vcable V | Vtotal V | Ptotal kW
Dip | 1 | 0.43 | 1.42 | 98 | 12 | 110 | 156
WQ | 1 | 0.52 | 1.48 | 38 | 12 | 50 | 75
SQ | 1 | 0.48 | 1.45 | 15 | 12 | 27 | 39
TCR1 Quad_CR_Type Power Converters
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 8
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 9
PARAMETER | DPC | QPCTYPE1 | QPCTYPE2 | QPCTYPE3 | SPC | OPC | CPC
MAINS | AC 20kV 50Hz T | AC 400 V 50Hz TN-S |  |  |  |  | 
IOUT MAX | 1450 A | 1500 A |  |  | 500 A | 30A | 6/14/20 A
VOUTMAX | 2750 | 200 V | 100 V | 50 V | 100 V | 90V | 75/75/40 V
ΔIOUT/IOUT | 10ppm | 100ppm |  |  | 0.1% | 1% | 1%
LONG TERM STABILITY | 10ppm | 100ppm |  |  | 0.1% | 1% | 1%
CONTROL | GSI CONTROL UNIT |  |  |  |  |  | 
DCCT | GSI CONTROL UNIT |  |  |  | Built In | Built In | 
MAX POWER | 4MW | 300kW | 150kW | 75kW | 50kW | 2.7kW | < 1kW
CR MAGNETS POWER CONVERTERS PARAMETERS
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 10
POWER CONVERTERS LOCATION
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 11
POWER CONVERTERS LOCATION
Blue – QPC, Indigo – SPC, Yellow – OPC&CPC
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 12
POWER CONVERTERS SETUP
High Power part. It is supplied by a 20kV, 3-phase Common supply system C2
Control part. It is supplied by a 400V, 3-phase Common supply system C2
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 13
POWER CONVERTERS SETUP
High Power part. It is supplied by a 400V, 3-phase Common supply system C2
Control part. It is supplied by a 400V, 3-phase Common supply system C2
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 14: DIP MAGNETS POWER CONVERTER DIAGRAM
20kVAC
MAINS
5.2 MVA
Step-Down
TRANSFORMER
+ POLARITY
12 pulse SCR RECTIFIER
POLARITY
12 pulse SCR
RECTIFIER
DCCT
DIP
MAGNETS
1.5kA
OUTPUT
FILTER
1.5kA 2750V
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 15: QUAD MAGNETS POWER CONVERTER DIAGRAM
400VAC
MAINS
Step-Down
TRANSFORMER
RECTIFIER
IGBT
H-BRIDGE
1.5kA 600V
20kHz
OUTPUT
FILTER
DCCT
QUAD
MAGNETS
1.5kA
OUTPUT
FILTER
IGBT
H-BRIDGE
1.5kA 600V
20kHz
IGBT
H-BRIDGE
6x250A 600V
20kHz
OUTPUT
FILTER
1.5kA 200V
TYPE1
1.5kA 100V
TYPE2
1.5kA 50V
TYPE3
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 16: SEXTUPOLE MAGNETS POWER CONVERTER DIAGRAM
400VAC
MAINS
Step-Down
TRANSFORMER
RECTIFIER
DCCT
SEXT
MAGNETS
500A
OUTPUT
FILTER
IGBT
H-BRIDGE
1.5kA 600V
20kHz
IGBT
H-BRIDGE
2x250A 600V
20kHz
OUTPUT
FILTER
500A 100V
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 17: OCTUPOLE MAGNETS POWER CONVERTER DIAGRAMM
400VAC
MAINS
3kW
100 V OUT
AC/DC
DCCT
OCT
MAGNET
30A
IGBT
H-BRIDGE
20kHz
OUTPUT
FILTER
30A 90V
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 18: 3MVA (1kA 3kV) ČKD DC SOURCE
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 19: QUAD POWER APPEARANCE
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 20: SEXTUPOLES POWER CONVERTER RACK LAYOUT
500A
Power Section
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 21: DIPOLE POWER CONVERTER CONTROL DIAGRAMM
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 22: QUAD POWER CONVERTER CONTROL
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 23: SEXTUPOLE POWER CONVERTER CONTROL
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 24
POWER CONVERTERS CONNECTIONS
Connection to electrical power : TN-S
Connection to load:
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 25: OCTUPOLE & STEERER POWER CONVERTERS RACK LAYOUT
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 26: OCT. & CORR. POWER BLOCKS
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 27: Current status
Concept
Discussed and agreed
Specifications
Ready
Design
Prototyped
CDR
Under release
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 28: PSS SYSTEM
QuadType PC with integrated PSS System
TCR1 DPC
CR QPC Type3
Need to understand
Is it enough?
How many QPC needs PSS
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019

## Slide 29: Thank you for attention
3nd Joint BINP-FAIR CC Workshop
25.11 - 28.11.2019